## Slide 1
Design and Implementation of Pilot of a TVET Renewable Energy Course
DELIVERABLE #5 - TRAINING COURSES & PROFESSIONAL DEVELOPMENT

## Slide 2: Irradiance Lab Results
These slides demonstrate the lab called Lab 5 PV Panel Angle of Incidence.
The pictures were taken under various irradiance values.
The set up was outside ambient temperature 12C.

## Slide 3: Irradiance Lab Results
The shorting wire was used to keep the MC-4 connectors from being opened under load.
The current was measured with a clamp on Ammeter attached to a multimeter.
Handheld pyranometer used to measure the irradiance.
Picture courtesy Author

## Slide 4: Irradiance Lab Results
The conditions for doing this lab was perfect.
The measured irradiance was very close to 1000W/m2
Ambient temperature was 12C.

## Slide 5: Irradiance Lab Results
The PV panel was
Hanwha Solar One
HSL60P6-PB-4-250
Voc = 37.7V
Isc = 8.79A
Picture courtesy Author

## Slide 6: Irradiance Lab Results
Ammeter / multimeter.
The shorting wire is
Connected to the panel.
Picture courtesy Author

## Slide 7: Irradiance Lab Results
The pyranometer reading 994 W/m2
Picture courtesy Author

## Slide 8: Irradiance Lab Results
The Ammeter showing 8.8A.
Isc is rated at 8.79A
Picture courtesy Author

## Slide 9: Irradiance Lab Results
The Voc is measured at
37.2 Volts
Voc rated at 37.7 V
Picture courtesy Author

## Slide 10: Irradiance Lab Results
The pyranometer reading 660 W/m2
Picture courtesy Author

## Slide 11: Irradiance Lab Results
The Ammeter showing 6.0A.
The irradiance is 66%
of the rated 1000W/m2
66% of the rated Isc.
0.66 x 8.79A = 5.8A
This is very close to
our reading of 6.0A.
Picture courtesy Author

## Slide 12: Irradiance Lab Results
The pyranometer reading 475 W/m2
Picture courtesy Author

## Slide 13: Irradiance Lab Results
The Ammeter showing 4.0A.
The irradiance is 45.7%
of the rated 100W/m2
46% of the rated Isc.
0.46 x 8.79A = 4.18A
This is very close to
our reading of 4.0A.
The readings were a
few seconds apart.
Picture courtesy Author

## Slide 14: Irradiance Lab Results
The pyranometer reading 116 W/m2
Picture courtesy Author

## Slide 15: Irradiance Lab Results
The Ammeter showing 0.9A.
The irradiance is 11%
of the rated 1000W/m2
11% of the rated Isc.
0.11 x 8.79A = 0.98A
This is very close to
our reading of 0.9 A.
Picture courtesy Author

## Slide 16: Irradiance Lab Results
The Voc is measured at only 32.2 Volts.
At this low irradiance
of 115 W/m2 which is
lower than the
200 W/m2 lower limit.
Voc rated at 37.7 V
Picture courtesy Author